## Metadata
doc_no | TJC-LLD-DS-CT-7801
revision | Rev 3
revision_status | Issued for Operation
document_type | Equipment Datasheet
equipment_tag | CT-7801
equipment_id | EQ-1000078011
equipment_name | COOLING TOWER CELL FAN
equipment_type | Induced Draft Cooling Tower Fan
plant_unit | Linear Low Density Polyethylene (LLDPE) Unit
area | 7800 – Cooling Water System
functional_location | TJC-LLD-7800-01
criticality | Non Critical
service | Induced draft cooling of circulating water for LLDPE unit
project | SDK Polyolefin Expansion Project
pid_reference | TJC-LLD-PID-7801
interlock_reference | SEQ-7801
vendor | Vendor ABC
driver_supplier | Supplier XYZ
source_file | Equipment Datasheet - CT-7801.pdf

## Design & Mechanical Data
category | parameter | value | unit
Design & Mechanical | Tower Type | INDUCED DRAFT, COUNTERFLOW, CELL 1 | —
Design & Mechanical | Blade Material | FRP (GRP) | —
Design & Mechanical | Fan Diameter | 7300 mm (24 ft) | —
Design & Mechanical | Drive Shaft | COMPOSITE FLOATING SHAFT | —
Design & Mechanical | Fan Type | AXIAL, 6 FRP BLADES | —
Design & Mechanical | Water Flow (Cell) | 2200 | m3/h
Design & Mechanical | Air Flow | 1,150,000 | m3/h
Design & Mechanical | Range / Approach | 10 degC / 4 degC | —
Design & Mechanical | Fan Speed | 128 | rpm
Design & Mechanical | Drift Eliminator | PVC CELLULAR | —
Design & Mechanical | Gearbox Ratio | 11.3 : 1 RIGHT ANGLE | —
Design & Mechanical | Fill | PVC FILM FILL | —
Design & Mechanical | Gearbox Oil | ISO VG 220 (4.5 L) | —

## Driver Data
category | parameter | value | unit
Driver / Motor Data | Output | 55 | kW
Driver / Motor Data | Enclosure | TEFC IP56 (wet duty) | —
Driver / Motor Data | Poles | 6 POLE | —
Driver / Motor Data | Area Classification | NON-HAZARDOUS | —
Driver / Motor Data | Speed | 970 | rpm
Driver / Motor Data | Mounting | IN-DUCT, WET | —
Driver / Motor Data | Voltage | 380 V / 3 Ph / 50 Hz | —
Driver / Motor Data | Frame | IEC 250M | —
Driver / Motor Data | Rated Current | 104 | A
Driver / Motor Data | Weight (Motor) | 410 | kg
Driver / Motor Data | Insulation Class | F | —
Driver / Motor Data | Driver Type | Electric Motor via Gearbox, TEFC | —