## Metadata
doc_no | TJC-LLD-IL-CT-7801
work_no | BA-0256
revision | Rev 3
document_type | Interlock Logic Diagram & Cause/Effect Matrix
logic_no | SEQ-7801
logic_description | COOLING TOWER FAN (CT-7801) SHUTDOWN LOGIC
sil_level | SIL 1
equipment_tag | CT-7801
functional_location | TJC-LLD-7800-01
pid_reference | TJC-LLD-PID-7801
datasheet_reference | TJC-LLD-DS-CT-7801
project | SDK Polyolefin Expansion Project
source_file | Interlock Logic Diagram - CT-7801.pdf

## Cause Effect
logic_no | trip_id | initiator_description | tag | set_point | voting | eff_1_trip_motor | eff_2_alarm | eff_3_start_spare
SEQ-7801 | T1 | Fan/gearbox vibration HIGH-HIGH | VSHH-7802 | > 9 mm/s | 1oo1 | X | X | X
SEQ-7801 | T2 | Gearbox oil temperature HIGH-HIGH | TSHH-7803 | > 90 degC | 1oo1 | X | X | X
SEQ-7801 | T3 | Gearbox oil pressure LOW | PSL-7807 | < 0.8 barg | 1oo1 | X | X | —
SEQ-7801 | T4 | Fan motor overload | MPR-7801 | MPR pickup | 1oo1 | X | X | X
effect_id | final_element_action
EFF-1 | TRIP FAN MOTOR CT-7801
EFF-2 | ANNUNCIATE ALARM ON DCS
EFF-3 | REQUEST START OF SPARE CELL CT-7802

## Start Permissive
logic_no | permissive_no | description | signal_tag | gate_logic
SEQ-7801 | P1 | Gearbox oil level OK | LG gearbox | AND
SEQ-7801 | P2 | Basin level normal (> LSL-7804) | LT-7804 | AND
SEQ-7801 | P3 | No fan lockout / maintenance key released | lockout | AND
— | — | ALL permissives TRUE → START CT-7801 ENABLED | — | AND