## Barscreen Cleaning
opl_no | OPL-CT-7801-01
opl_title | Barscreen Cleaning (Suction Screen)
sheet | 1 of 1
discipline | Process / Operations
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Basic Knowledge
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Wednesday, 27 May 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-01 - Barscreen_Cleaning_Suction_Screen.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains barscreen cleaning (suction screen) for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. A clogged barscreen starves the circulating water pumps and fouls the fill, reducing cooling for the whole unit. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Obtain the correct operating permit and brief the shift team before the task.
Safety Precautions | Precaution 2 | Confirm hazardous fluids are isolated / inerted as required by procedure.
Safety Precautions | Precaution 3 | Beware of flammable, hot, or high-pressure fluids; wear the correct PPE.
Safety Precautions | Precaution 4 | Never defeat a safety interlock or trip without an authorised override permit.
Safety Precautions | Precaution 5 | Have emergency actions and communications ready before starting.
Tools & Materials | Tool 1 | Operating procedure & P&ID
Tools & Materials | Tool 2 | Radio / communication with panel
Tools & Materials | Tool 3 | Gas detector (O2 / LEL) as required
Tools & Materials | Tool 4 | Correct PPE for the fluid handled
Tools & Materials | Tool 5 | Sample containers & PPE for sampling
Tools & Materials | Tool 6 | Permit-to-work documentation
Procedure | Step 1 - Action | Rake the SS304 barscreen every shift on the round
Procedure | Step 1 - Check | Permit valid & briefed
Procedure | Step 2 - Action | Remove leaves, debris and biological growth
Procedure | Step 2 - Check | Parameter within limit
Procedure | Step 3 - Action | Check the differential level across the screen
Procedure | Step 3 - Check | Interlock status confirmed
Procedure | Step 4 - Action | Dispose of debris correctly and log the cleaning
Procedure | Step 4 - Check | Change logged on DCS
Procedure | Step 5 - Action | Report rapid re-fouling to water treatment
Procedure | Step 5 - Check | Handover to next shift
Common Problems | Symptom 1 | Routine barscreen cleaning on operator round
Common Problems | Likely Cause 1 | Normal debris accumulation
Common Problems | Action 1 | Raked barscreen clear, checked differential level
Common Problems | Symptom 2 | Scheduled fan gearbox oil change
Common Problems | Likely Cause 2 | Routine - oil sample acceptable
Common Problems | Action 2 | Drained and refilled ISO VG 220, replaced breather
Common Problems | Symptom 3 | VSHH-7802 vibration alarm on CT-7801 fan
Common Problems | Likely Cause 3 | Leading-edge erosion on one FRP blade caused imbalance
Common Problems | Action 3 | Inspected blades, re-balanced fan, vibration normalised
Key Learning Points | Point 1 | A clogged barscreen starves the circulating water pumps and fouls the fill, reducing cooling for the whole unit.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Gearbox Oil Level & Change
opl_no | OPL-CT-7801-02
opl_title | Gearbox Oil Level & Change (ISO VG 220)
sheet | 1 of 1
discipline | Mechanical
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Basic Knowledge
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Sunday, 31 May 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-02 - Gearbox_Oil_Level_Change_ISO_VG_220.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains gearbox oil level & change (iso vg 220) for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. Low or degraded gearbox oil causes overheating (TSHH-7803) and gear failure high up on the fan deck. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Apply LOTO (Lock-Out Tag-Out) and prove zero energy before starting work.
Safety Precautions | Precaution 2 | Isolate, depressurise, drain and purge the equipment; obtain a valid work permit.
Safety Precautions | Precaution 3 | Wear the correct PPE: coverall, safety shoes, gloves, goggles and hearing protection.
Safety Precautions | Precaution 4 | Beware of stored mechanical energy (springs, rotating inertia) and pinch points.
Safety Precautions | Precaution 5 | Use certified lifting gear and correct manual-handling technique for heavy parts.
Tools & Materials | Tool 1 | Standard mechanical hand tools & calibrated torque wrench
Tools & Materials | Tool 2 | LOTO padlocks and permit
Tools & Materials | Tool 3 | Laser/dial alignment kit (as applicable)
Tools & Materials | Tool 4 | Feeler gauges, dial indicator, seal/bearing pullers
Tools & Materials | Tool 5 | Correct spare parts and gaskets per the BOM
Tools & Materials | Tool 6 | Lifting gear and slings (certified)
Procedure | Step 1 - Action | Check the gearbox sight-glass oil level
Procedure | Step 1 - Check | Isolation & LOTO verified
Procedure | Step 2 - Action | Sample the oil for water contamination and metal
Procedure | Step 2 - Check | Parts match BOM / spec
Procedure | Step 3 - Action | Change the ISO VG 220 (4.5 L) per the schedule
Procedure | Step 3 - Check | Torque / clearance to spec
Procedure | Step 4 - Action | Verify the oil pressure PSL-7807 after refill
Procedure | Step 4 - Check | No leak / smooth operation
Procedure | Step 5 - Action | Record the oil change and next due date
Procedure | Step 5 - Check | Record in equipment history
Common Problems | Symptom 1 | Scheduled fan gearbox oil change
Common Problems | Likely Cause 1 | Routine - oil sample acceptable
Common Problems | Action 1 | Drained and refilled ISO VG 220, replaced breather
Common Problems | Symptom 2 | VSHH-7802 vibration alarm on CT-7801 fan
Common Problems | Likely Cause 2 | Leading-edge erosion on one FRP blade caused imbalance
Common Problems | Action 2 | Inspected blades, re-balanced fan, vibration normalised
Common Problems | Symptom 3 | TSHH-7803 gearbox oil temperature rising
Common Problems | Likely Cause 3 | Degraded oil and fouled oil cooler
Common Problems | Action 3 | Changed oil, cleaned oil cooler, verified temperature
Key Learning Points | Point 1 | Low or degraded gearbox oil causes overheating (TSHH-7803) and gear failure high up on the fan deck.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Fan Blade Inspection & Balance
opl_no | OPL-CT-7801-03
opl_title | Fan Blade Inspection & Balance (FRP)
sheet | 1 of 1
discipline | Mechanical
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Improvement
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Thursday, 04 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-03 - Fan_Blade_Inspection_Balance_FRP.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains fan blade inspection & balance (frp) for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. A cracked or eroded FRP blade unbalances the fan and causes the VSHH-7802 vibration trip. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Apply LOTO (Lock-Out Tag-Out) and prove zero energy before starting work.
Safety Precautions | Precaution 2 | Isolate, depressurise, drain and purge the equipment; obtain a valid work permit.
Safety Precautions | Precaution 3 | Wear the correct PPE: coverall, safety shoes, gloves, goggles and hearing protection.
Safety Precautions | Precaution 4 | Beware of stored mechanical energy (springs, rotating inertia) and pinch points.
Safety Precautions | Precaution 5 | Use certified lifting gear and correct manual-handling technique for heavy parts.
Tools & Materials | Tool 1 | Standard mechanical hand tools & calibrated torque wrench
Tools & Materials | Tool 2 | LOTO padlocks and permit
Tools & Materials | Tool 3 | Laser/dial alignment kit (as applicable)
Tools & Materials | Tool 4 | Feeler gauges, dial indicator, seal/bearing pullers
Tools & Materials | Tool 5 | Correct spare parts and gaskets per the BOM
Tools & Materials | Tool 6 | Lifting gear and slings (certified)
Procedure | Step 1 - Action | Lock out the fan and inspect all 6 FRP blades
Procedure | Step 1 - Check | Isolation & LOTO verified
Procedure | Step 2 - Action | Check for cracks, leading-edge erosion and tip clearance
Procedure | Step 2 - Check | Parts match BOM / spec
Procedure | Step 3 - Action | Verify the blade pitch angle is uniform on all blades
Procedure | Step 3 - Check | Torque / clearance to spec
Procedure | Step 4 - Action | Re-balance the fan if vibration is high
Procedure | Step 4 - Check | No leak / smooth operation
Procedure | Step 5 - Action | Torque the blade root bolts to specification
Procedure | Step 5 - Check | Record in equipment history
Common Problems | Symptom 1 | Scheduled fan gearbox oil change
Common Problems | Likely Cause 1 | Routine - oil sample acceptable
Common Problems | Action 1 | Drained and refilled ISO VG 220, replaced breather
Common Problems | Symptom 2 | VSHH-7802 vibration alarm on CT-7801 fan
Common Problems | Likely Cause 2 | Leading-edge erosion on one FRP blade caused imbalance
Common Problems | Action 2 | Inspected blades, re-balanced fan, vibration normalised
Common Problems | Symptom 3 | TSHH-7803 gearbox oil temperature rising
Common Problems | Likely Cause 3 | Degraded oil and fouled oil cooler
Common Problems | Action 3 | Changed oil, cleaned oil cooler, verified temperature
Key Learning Points | Point 1 | A cracked or eroded FRP blade unbalances the fan and causes the VSHH-7802 vibration trip.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Circulating Water pH
opl_no | OPL-CT-7801-04
opl_title | Circulating Water pH Control (AI-7805)
sheet | 1 of 1
discipline | Process / Operations
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Improvement
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Monday, 08 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-04 - Circulating_Water_pH_Control_AI_7805.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains circulating water ph control (ai-7805) for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. Wrong pH causes scaling or corrosion across the entire cooling water loop, not just this cell. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Obtain the correct operating permit and brief the shift team before the task.
Safety Precautions | Precaution 2 | Confirm hazardous fluids are isolated / inerted as required by procedure.
Safety Precautions | Precaution 3 | Beware of flammable, hot, or high-pressure fluids; wear the correct PPE.
Safety Precautions | Precaution 4 | Never defeat a safety interlock or trip without an authorised override permit.
Safety Precautions | Precaution 5 | Have emergency actions and communications ready before starting.
Tools & Materials | Tool 1 | Operating procedure & P&ID
Tools & Materials | Tool 2 | Radio / communication with panel
Tools & Materials | Tool 3 | Gas detector (O2 / LEL) as required
Tools & Materials | Tool 4 | Correct PPE for the fluid handled
Tools & Materials | Tool 5 | Sample containers & PPE for sampling
Tools & Materials | Tool 6 | Permit-to-work documentation
Procedure | Step 1 - Action | Read the AI-7805 pH each shift (target 7.0-8.5)
Procedure | Step 1 - Check | Permit valid & briefed
Procedure | Step 2 - Action | Check the acid / caustic dosing pumps are running
Procedure | Step 2 - Check | Parameter within limit
Procedure | Step 3 - Action | Cross-check against a manual lab titration
Procedure | Step 3 - Check | Interlock status confirmed
Procedure | Step 4 - Action | Adjust the dosing set-point as needed
Procedure | Step 4 - Check | Change logged on DCS
Procedure | Step 5 - Action | Report large pH swings to water treatment
Procedure | Step 5 - Check | Handover to next shift
Common Problems | Symptom 1 | Routine barscreen cleaning on operator round
Common Problems | Likely Cause 1 | Normal debris accumulation
Common Problems | Action 1 | Raked barscreen clear, checked differential level
Common Problems | Symptom 2 | Scheduled fan gearbox oil change
Common Problems | Likely Cause 2 | Routine - oil sample acceptable
Common Problems | Action 2 | Drained and refilled ISO VG 220, replaced breather
Common Problems | Symptom 3 | VSHH-7802 vibration alarm on CT-7801 fan
Common Problems | Likely Cause 3 | Leading-edge erosion on one FRP blade caused imbalance
Common Problems | Action 3 | Inspected blades, re-balanced fan, vibration normalised
Key Learning Points | Point 1 | Wrong pH causes scaling or corrosion across the entire cooling water loop, not just this cell.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Drift Eliminator & Fill
opl_no | OPL-CT-7801-05
opl_title | Drift Eliminator & Fill Inspection
sheet | 1 of 1
discipline | Mechanical
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Basic Knowledge
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Friday, 12 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-05 - Drift_Eliminator_Fill_Inspection.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains drift eliminator & fill inspection for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. Fouled or collapsed fill and drift eliminators cut the cooling performance and raise the basin temperature. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Apply LOTO (Lock-Out Tag-Out) and prove zero energy before starting work.
Safety Precautions | Precaution 2 | Isolate, depressurise, drain and purge the equipment; obtain a valid work permit.
Safety Precautions | Precaution 3 | Wear the correct PPE: coverall, safety shoes, gloves, goggles and hearing protection.
Safety Precautions | Precaution 4 | Beware of stored mechanical energy (springs, rotating inertia) and pinch points.
Safety Precautions | Precaution 5 | Use certified lifting gear and correct manual-handling technique for heavy parts.
Tools & Materials | Tool 1 | Standard mechanical hand tools & calibrated torque wrench
Tools & Materials | Tool 2 | LOTO padlocks and permit
Tools & Materials | Tool 3 | Laser/dial alignment kit (as applicable)
Tools & Materials | Tool 4 | Feeler gauges, dial indicator, seal/bearing pullers
Tools & Materials | Tool 5 | Correct spare parts and gaskets per the BOM
Tools & Materials | Tool 6 | Lifting gear and slings (certified)
Procedure | Step 1 - Action | Inspect the PVC fill for scaling and collapse
Procedure | Step 1 - Check | Isolation & LOTO verified
Procedure | Step 2 - Action | Check the drift eliminator packs are aligned
Procedure | Step 2 - Check | Parts match BOM / spec
Procedure | Step 3 - Action | Hose down fouled sections during a cell outage
Procedure | Step 3 - Check | Torque / clearance to spec
Procedure | Step 4 - Action | Report a thermal performance drop via TT-7801
Procedure | Step 4 - Check | No leak / smooth operation
Procedure | Step 5 - Action | Plan fill replacement if degradation is widespread
Procedure | Step 5 - Check | Record in equipment history
Common Problems | Symptom 1 | Scheduled fan gearbox oil change
Common Problems | Likely Cause 1 | Routine - oil sample acceptable
Common Problems | Action 1 | Drained and refilled ISO VG 220, replaced breather
Common Problems | Symptom 2 | VSHH-7802 vibration alarm on CT-7801 fan
Common Problems | Likely Cause 2 | Leading-edge erosion on one FRP blade caused imbalance
Common Problems | Action 2 | Inspected blades, re-balanced fan, vibration normalised
Common Problems | Symptom 3 | TSHH-7803 gearbox oil temperature rising
Common Problems | Likely Cause 3 | Degraded oil and fouled oil cooler
Common Problems | Action 3 | Changed oil, cleaned oil cooler, verified temperature
Key Learning Points | Point 1 | Fouled or collapsed fill and drift eliminators cut the cooling performance and raise the basin temperature.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Gearbox Vibration Monitoring
opl_no | OPL-CT-7801-06
opl_title | Gearbox Vibration Monitoring (VSHH-7802)
sheet | 1 of 1
discipline | Instrument
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Improvement
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Tuesday, 16 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-06 - Gearbox_Vibration_Monitoring_VSHH_7802.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains gearbox vibration monitoring (vshh-7802) for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. A rising vibration trend warns of gear or bearing wear before the fan trips or throws a blade. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | De-energise and isolate the loop; place the function to bypass/inhibit under permit.
Safety Precautions | Precaution 2 | Inform the panel operator before working on any trip, valve or transmitter.
Safety Precautions | Precaution 3 | Take care with instrument air / hydraulic pressure when disconnecting tubing.
Safety Precautions | Precaution 4 | Verify intrinsic-safety / Ex integrity is restored before returning to service.
Safety Precautions | Precaution 5 | Wear correct PPE and follow ESD/override control procedures.
Tools & Materials | Tool 1 | HART communicator / positioner software (e.g. ValveLink)
Tools & Materials | Tool 2 | Loop calibrator & decade box / pressure source
Tools & Materials | Tool 3 | Digital multimeter and clamp meter
Tools & Materials | Tool 4 | Span/zero test gas or reference standards
Tools & Materials | Tool 5 | Torque screwdriver and small hand tools
Tools & Materials | Tool 6 | Certified test/inhibit permit
Procedure | Step 1 - Action | Trend the VS-7802 reading on the PdM route
Procedure | Step 1 - Check | Loop isolated / under permit
Procedure | Step 2 - Action | Alarm at 6 mm/s and trip at 9 mm/s (VSHH-7802)
Procedure | Step 2 - Check | Reference standard traceable
Procedure | Step 3 - Action | Correlate the rise with gearbox oil temperature TE-7803
Procedure | Step 3 - Check | As-found & as-left recorded
Procedure | Step 4 - Action | Inspect the floating drive-shaft couplings
Procedure | Step 4 - Check | Trip / control action verified
Procedure | Step 5 - Action | Escalate a step-change to reliability
Procedure | Step 5 - Check | Return to service confirmed
Common Problems | Symptom 1 | Scheduled pH analyzer calibration
Common Problems | Likely Cause 1 | Electrode drift
Common Problems | Action 1 | Recalibrated AI-7805 on buffer solutions, replaced electrode
Common Problems | Symptom 2 | Blowdown conductivity reading unreliable
Common Problems | Likely Cause 2 | Conductivity cell fouled with scale
Common Problems | Action 2 | Cleaned and recalibrated AI-7806 conductivity cell
Common Problems | Symptom 3 | Routine barscreen cleaning on operator round
Common Problems | Likely Cause 3 | Normal debris accumulation
Common Problems | Action 3 | Raked barscreen clear, checked differential level
Key Learning Points | Point 1 | A rising vibration trend warns of gear or bearing wear before the fan trips or throws a blade.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Conductivity & Blowdown Control
opl_no | OPL-CT-7801-07
opl_title | Conductivity / Blowdown Control (AI-7806)
sheet | 1 of 1
discipline | Process / Operations
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area_unit | 7800 - COOLING TOWER SYSTEM
related_interlock | SEQ-7801 (SIL 1)
pid_reference | TJC-LLD-PID-7801
classification | Improvement
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Wahyu Setiadi (EMP-1113)
approved_by | Arya Wibisono (EMP-0912)
date_of_sharing | Saturday, 20 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-CT-7801-07 - Conductivity_Blowdown_Control_AI_7806.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains conductivity / blowdown control (ai-7806) for CT-7801 (COOLING TOWER CELL FAN) in the COOLING TOWER SYSTEM. High conductivity means the water is over-concentrated; automatic blowdown keeps the cycles of concentration in range. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Obtain the correct operating permit and brief the shift team before the task.
Safety Precautions | Precaution 2 | Confirm hazardous fluids are isolated / inerted as required by procedure.
Safety Precautions | Precaution 3 | Beware of flammable, hot, or high-pressure fluids; wear the correct PPE.
Safety Precautions | Precaution 4 | Never defeat a safety interlock or trip without an authorised override permit.
Safety Precautions | Precaution 5 | Have emergency actions and communications ready before starting.
Tools & Materials | Tool 1 | Operating procedure & P&ID
Tools & Materials | Tool 2 | Radio / communication with panel
Tools & Materials | Tool 3 | Gas detector (O2 / LEL) as required
Tools & Materials | Tool 4 | Correct PPE for the fluid handled
Tools & Materials | Tool 5 | Sample containers & PPE for sampling
Tools & Materials | Tool 6 | Permit-to-work documentation
Procedure | Step 1 - Action | Read the AI-7806 conductivity value
Procedure | Step 1 - Check | Permit valid & briefed
Procedure | Step 2 - Action | Verify the automatic blowdown valve XV-7806 operates
Procedure | Step 2 - Check | Parameter within limit
Procedure | Step 3 - Action | Maintain the target cycles of concentration
Procedure | Step 3 - Check | Interlock status confirmed
Procedure | Step 4 - Action | Log make-up versus blowdown volumes
Procedure | Step 4 - Check | Change logged on DCS
Procedure | Step 5 - Action | Coordinate chemical dosing with water treatment
Procedure | Step 5 - Check | Handover to next shift
Common Problems | Symptom 1 | Routine barscreen cleaning on operator round
Common Problems | Likely Cause 1 | Normal debris accumulation
Common Problems | Action 1 | Raked barscreen clear, checked differential level
Common Problems | Symptom 2 | Scheduled fan gearbox oil change
Common Problems | Likely Cause 2 | Routine - oil sample acceptable
Common Problems | Action 2 | Drained and refilled ISO VG 220, replaced breather
Common Problems | Symptom 3 | VSHH-7802 vibration alarm on CT-7801 fan
Common Problems | Likely Cause 3 | Leading-edge erosion on one FRP blade caused imbalance
Common Problems | Action 3 | Inspected blades, re-balanced fan, vibration normalised
Key Learning Points | Point 1 | High conductivity means the water is over-concentrated; automatic blowdown keeps the cycles of concentration in range.
Key Learning Points | Point 2 | Respect the interlock SEQ-7801: e.g. VSHH-7802 trips at > 9 mm/s - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-7801 before working on CT-7801.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.