## Metadata
doc_no | TJC-LLD-PID-7801
document_type | Piping & Instrumentation Diagram (P&ID)
title | P&ID: COOLING TOWER FAN (CT-7801) SYSTEM
equipment_tag | CT-7801
equipment_name | COOLING TOWER CELL FAN
area | 7800 – Cooling Water System
plant_unit | Linear Low Density Polyethylene (LLDPE) Unit
functional_location | TJC-LLD-7800-01
datasheet_reference | TJC-LLD-DS-CT-7801
interlock_reference | SEQ-7801
source_file | P&ID_Set 7.png
file_type | PNG (Visual Diagram)
notes | Motor Specs: 55 kW, TEFC IP56, Area Non-hazardous, 380 V/3 Ph/50 Hz. Axial induced draft fan 6 FRP blades. Composite Drive Shaft Arrangement.

## Instrument List
tag | description | instrument_type | set_point | unit | function | related_interlock | location
VSHH-7802 | Fan/gearbox vibration HIGH-HIGH | Vibration Switch | > 9 | mm/s | Cause T1 (Trip Fan Motor CT-7801) | T1/EFF-1/EFF-2/EFF-3 | Fan Drive Shaft / Gearbox
TSHH-7803 | Gearbox oil temperature HIGH-HIGH | Temp Switch | > 90 | degC | Cause T2 (Trip Fan Motor CT-7801) | T2/EFF-1/EFF-2/EFF-3 | Fan Gearbox
PSL-7807 | Gearbox oil pressure LOW | Pressure Switch | < 0.8 | barg | Cause T3 (Trip Fan Motor CT-7801) | T3/EFF-1/EFF-2 | Gearbox lube oil system
MPR-7801 | Fan motor overload relay | Motor Protection | MPR pickup | — | Cause T4 (Trip Fan Motor CT-7801) | T4/EFF-1/EFF-2/EFF-3 | Motor MCC Panel
LG gearbox | Gearbox oil sight glass / level gauge | Level Gauge | — | — | Permissive P1 (LG Gearbox oil level OK) | P1 | Fan Gearbox
LT-7804 | Basin level transmitter | Level Transmitter | > LSL-7804 | — | Permissive P2 (Basin level normal) | P2 | Cooling Tower Basin
Lockout Key | Maintenance lockout switch | Hand Switch | — | — | Permissive P3 (Lockout release logic) | P3 | Motor MCC / Field
AI-7805 | Circulating Water pH Analyzer | Analyzer (pH) | 7.0-8.5 | pH | Monitoring & Dosing Control (dari OPL) | — | Cooling water return line
AI-7806 | Conductivity Analyzer | Analyzer (Cond) | — | µS/cm | Blowdown Control (dari OPL) | — | Cooling water basin/return