## Metadata
doc_no | TJC-LLD-DS-LV-6701
revision | Rev 3
revision_status | Issued for Operation
document_type | Equipment Datasheet
equipment_tag | LV-6701
equipment_id | EQ-1000067011
equipment_name | SEPARATOR LEVEL CONTROL VALVE
equipment_type | Globe Control Valve + Diaphragm Actuator
plant_unit | Linear Low Density Polyethylene (LLDPE) Unit
area | 6700 – Product Separation
functional_location | TJC-LLD-6700-01
criticality | Low Critical
service | Level control of LP Separator FA-6710 bottoms to downstream
project | SDK Polyolefin Expansion Project
pid_reference | TJC-LLD-PID-6701
interlock_reference | SEQ-6701
vendor | Vendor ABC
driver_supplier | Supplier XYZ
source_file | Equipment Datasheet - LV-6701.pdf

## Design & Mechanical Data
category | parameter | value | unit
Design & Mechanical | Valve Type | GLOBE, CAGE-GUIDED, ED | —
Design & Mechanical | Fail Action | FAIL CLOSED (FC) | —
Design & Mechanical | Actuator | FISHER 667 SIZE 45 | —
Design & Mechanical | Body Size | 3 inch (DN80) | —
Design & Mechanical | Positioner | DVC6200 HART, 4-20 mA | —
Design & Mechanical | Body Rating | ASME 300# | —
Design & Mechanical | Air Supply | 1.4 barg INSTRUMENT AIR | —
Design & Mechanical | Body Material | WCC CARBON STEEL | —
Design & Mechanical | Packing | PTFE V-RING | —
Design & Mechanical | Trim Material | SS316 + STELLITE | —
Design & Mechanical | Bench Set | 0.2-1.0 barg | —
Design & Mechanical | Trim Characteristic | EQUAL PERCENTAGE | —
Design & Mechanical | Handwheel | TOP-MOUNTED | —
Design & Mechanical | Rated CV | 110 | —
Design & Mechanical | Service Fluid | HEXANE + POLYMER BOTTOMS | —

## Driver Data
category | parameter | value | unit
Driver / Motor Data | Controller | LIC-6701 (on FA-6710 level) | —
Driver / Motor Data | Action on Air Fail | VALVE CLOSES | —
Driver / Motor Data | Input Signal | 4-20 mA | —
Driver / Motor Data | Solenoid | XV-6701 (ESD) | —
Driver / Motor Data | Stroke | 38 | mm
Driver / Motor Data | Limit Switch | ZSL/ZSH-6701 | —
Driver / Motor Data | Leakage Class | ANSI CLASS IV | —
Driver / Motor Data | Driver Type | Pneumatic Spring-Diaphragm Actuator | —