## Metadata
doc_no | TJC-LLD-IL-LV-6701
work_no | BA-0256
revision | Rev 3
document_type | Interlock Logic Diagram & Cause/Effect Matrix
logic_no | SEQ-6701
logic_description | LP SEPARATOR LEVEL PROTECTION (FA-6710 / LV-6701) LOGIC
sil_level | SIL 1
equipment_tag | LV-6701
functional_location | TJC-LLD-6700-01
pid_reference | TJC-LLD-PID-6701
datasheet_reference | TJC-LLD-DS-LV-6701
project | SDK Polyolefin Expansion Project
source_file | Interlock Logic Diagram - LV-6701.pdf

## Cause Effect
logic_no | trip_id | initiator_description | tag | set_point | voting | eff_1_open_fully | eff_2_close | eff_3_vent_actuator | eff_4_alarm
SEQ-6701 | T1 | Separator level HIGH-HIGH | LSHH-6710 | > 85 % | 1oo2 | X | — | — | X
SEQ-6701 | T2 | Separator level LOW-LOW | LSLL-6710 | < 15 % | 1oo2 | — | X | — | X
SEQ-6701 | T3 | ESD activation (manual) | HS-6701 | ESD signal | 1oo1 | — | — | X | X
SEQ-6701 | T4 | Instrument air pressure LOW | PSL-6702 | < 1.0 barg | 1oo1 | — | — | X | X
effect_id | final_element_action
EFF-1 | OPEN LV-6701 FULLY (relieve level)
EFF-2 | CLOSE LV-6701 (prevent gas blow-by)
EFF-3 | VENT ACTUATOR - LV-6701 FAILS CLOSED
EFF-4 | ANNUNCIATE ALARM ON DCS

## Start Permissive
logic_no | permissive_no | description | signal_tag | gate_logic
SEQ-6701 | P1 | Instrument air available (> 1.2 barg) | PI-6702 | AND
SEQ-6701 | P2 | Positioner DVC6200 in AUTO/healthy | DVC6200 | AND
SEQ-6701 | P3 | Bypass HV-6701 closed (normal operation) | HV-6701 | AND
— | — | ALL permissives TRUE → START LV-6701 ENABLED | — | AND