## Control Valve Stroke
opl_no | OPL-LV-6701-01
opl_title | Control Valve Stroke Calibration (DVC6200)
sheet | 1 of 1
discipline | Instrument
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Basic Knowledge
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Saturday, 16 May 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-01 - Control_Valve_Stroke_Calibration_DVC6200.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains control valve stroke calibration (dvc6200) for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. Correct mapping of the 4-20 mA signal to 0-100 % valve stroke is essential for stable separator level control. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | De-energise and isolate the loop; place the function to bypass/inhibit under permit.
Safety Precautions | Precaution 2 | Inform the panel operator before working on any trip, valve or transmitter.
Safety Precautions | Precaution 3 | Take care with instrument air / hydraulic pressure when disconnecting tubing.
Safety Precautions | Precaution 4 | Verify intrinsic-safety / Ex integrity is restored before returning to service.
Safety Precautions | Precaution 5 | Wear correct PPE and follow ESD/override control procedures.
Tools & Materials | Tool 1 | HART communicator / positioner software (e.g. ValveLink)
Tools & Materials | Tool 2 | Loop calibrator & decade box / pressure source
Tools & Materials | Tool 3 | Digital multimeter and clamp meter
Tools & Materials | Tool 4 | Span/zero test gas or reference standards
Tools & Materials | Tool 5 | Torque screwdriver and small hand tools
Tools & Materials | Tool 6 | Certified test/inhibit permit
Procedure | Step 1 - Action | Connect the HART communicator and establish link to DVC6200
Procedure | Step 1 - Check | Loop isolated / under permit
Procedure | Step 2 - Action | Run the Auto-Travel calibration routine in the positioner
Procedure | Step 2 - Check | Reference standard traceable
Procedure | Step 3 - Action | Step the 4-20mA signal (0, 25, 50, 75, 100%) and verify stroke
Procedure | Step 3 - Check | As-found & as-left recorded
Procedure | Step 4 - Action | Check fail-closed action on signal loss (4mA = 0%)
Procedure | Step 4 - Check | Trip / control action verified
Procedure | Step 5 - Action | Save the calibration signature to the asset management system
Procedure | Step 5 - Check | Return to service confirmed
Common Problems | Symptom 1 | LV-6701 not responding to LIC-6701, level control lost
Common Problems | Likely Cause 1 | Stem seized in PTFE packing (over-tightened + fines)
Common Problems | Action 1 | Freed stem, renewed packing, lubricated, re-stroked and calibrated
Common Problems | Symptom 2 | Positioner giving position error after drift
Common Problems | Likely Cause 2 | Positioner feedback out of calibration
Common Problems | Action 2 | Recalibrated DVC6200, updated firmware, verified travel
Common Problems | Symptom 3 | Hexane weeping at LV-6701 stem packing
Common Problems | Likely Cause 3 | PTFE V-ring packing worn
Common Problems | Action 3 | Renewed PTFE V-ring packing set, re-torqued gland
Key Learning Points | Point 1 | Correct mapping of the 4-20 mA signal to 0-100 % valve stroke is essential for stable separator level control.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Air Supply & Filter Regulator
opl_no | OPL-LV-6701-02
opl_title | Instrument Air Supply & Filter Regulator
sheet | 1 of 1
discipline | Instrument
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Trouble Case
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Wednesday, 20 May 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-02 - Instrument_Air_Supply_Filter_Regulator.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains instrument air supply & filter regulator for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. Dirty or low instrument air makes the valve sluggish or fail closed, upsetting FA-6710 level and tripping PSL-6702. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | De-energise and isolate the loop; place the function to bypass/inhibit under permit.
Safety Precautions | Precaution 2 | Inform the panel operator before working on any trip, valve or transmitter.
Safety Precautions | Precaution 3 | Take care with instrument air / hydraulic pressure when disconnecting tubing.
Safety Precautions | Precaution 4 | Verify intrinsic-safety / Ex integrity is restored before returning to service.
Safety Precautions | Precaution 5 | Wear correct PPE and follow ESD/override control procedures.
Tools & Materials | Tool 1 | HART communicator / positioner software (e.g. ValveLink)
Tools & Materials | Tool 2 | Loop calibrator & decade box / pressure source
Tools & Materials | Tool 3 | Digital multimeter and clamp meter
Tools & Materials | Tool 4 | Span/zero test gas or reference standards
Tools & Materials | Tool 5 | Torque screwdriver and small hand tools
Tools & Materials | Tool 6 | Certified test/inhibit permit
Procedure | Step 1 - Action | Check the PI-6702 air supply is at 1.4 barg
Procedure | Step 1 - Check | Loop isolated / under permit
Procedure | Step 2 - Action | Drain the filter regulator bowl of condensate
Procedure | Step 2 - Check | Reference standard traceable
Procedure | Step 3 - Action | Replace a clogged air filter element
Procedure | Step 3 - Check | As-found & as-left recorded
Procedure | Step 4 - Action | Confirm there are no air leaks on the tubing/fittings
Procedure | Step 4 - Check | Trip / control action verified
Procedure | Step 5 - Action | Verify PSL-6702 low-air alarm set-point
Procedure | Step 5 - Check | Return to service confirmed
Common Problems | Symptom 1 | LV-6701 not responding to LIC-6701, level control lost
Common Problems | Likely Cause 1 | Stem seized in PTFE packing (over-tightened + fines)
Common Problems | Action 1 | Freed stem, renewed packing, lubricated, re-stroked and calibrated
Common Problems | Symptom 2 | Positioner giving position error after drift
Common Problems | Likely Cause 2 | Positioner feedback out of calibration
Common Problems | Action 2 | Recalibrated DVC6200, updated firmware, verified travel
Common Problems | Symptom 3 | Hexane weeping at LV-6701 stem packing
Common Problems | Likely Cause 3 | PTFE V-ring packing worn
Common Problems | Action 3 | Renewed PTFE V-ring packing set, re-torqued gland
Key Learning Points | Point 1 | Dirty or low instrument air makes the valve sluggish or fail closed, upsetting FA-6710 level and tripping PSL-6702.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Packing Adjustment(PTFE V-Ring)
opl_no | OPL-LV-6701-03
opl_title | Packing Adjustment (PTFE V-Ring)
sheet | 1 of 1
discipline | Mechanical
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Trouble Case
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Sunday, 24 May 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-03 - Packing_Adjustment_PTFE_V_Ring.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains packing adjustment (ptfe v-ring) for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. Loose packing leaks hexane at the stem; over-tight packing makes the stem stick and the valve hunt. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Apply LOTO (Lock-Out Tag-Out) and prove zero energy before starting work.
Safety Precautions | Precaution 2 | Isolate, depressurise, drain and purge the equipment; obtain a valid work permit.
Safety Precautions | Precaution 3 | Wear the correct PPE: coverall, safety shoes, gloves, goggles and hearing protection.
Safety Precautions | Precaution 4 | Beware of stored mechanical energy (springs, rotating inertia) and pinch points.
Safety Precautions | Precaution 5 | Use certified lifting gear and correct manual-handling technique for heavy parts.
Tools & Materials | Tool 1 | Standard mechanical hand tools & calibrated torque wrench
Tools & Materials | Tool 2 | LOTO padlocks and permit
Tools & Materials | Tool 3 | Laser/dial alignment kit (as applicable)
Tools & Materials | Tool 4 | Feeler gauges, dial indicator, seal/bearing pullers
Tools & Materials | Tool 5 | Correct spare parts and gaskets per the BOM
Tools & Materials | Tool 6 | Lifting gear and slings (certified)
Procedure | Step 1 - Action | Isolate the line and depressurise before touching packing
Procedure | Step 1 - Check | Isolation & LOTO verified
Procedure | Step 2 - Action | Snug the packing nuts evenly in small increments
Procedure | Step 2 - Check | Parts match BOM / spec
Procedure | Step 3 - Action | Stroke the valve and check for a leak-free, smooth travel
Procedure | Step 3 - Check | Torque / clearance to spec
Procedure | Step 4 - Action | Do not over-torque - excessive friction degrades control
Procedure | Step 4 - Check | No leak / smooth operation
Procedure | Step 5 - Action | Record the packing adjustment in the valve history
Procedure | Step 5 - Check | Record in equipment history
Common Problems | Symptom 1 | Manual handwheel jack on LV-6701 seized
Common Problems | Likely Cause 1 | Corrosion in handwheel thread
Common Problems | Action 1 | Overhauled handwheel assembly, greased thread
Common Problems | Symptom 2 | LV-6701 passing when closed (Class IV exceeded)
Common Problems | Likely Cause 2 | Seat/plug erosion from polymer bottoms
Common Problems | Action 2 | Lapped seat and plug, restored Class IV shut-off
Common Problems | Symptom 3 | Minor weep at body/bonnet joint
Common Problems | Likely Cause 3 | Spiral-wound body gasket relaxed
Common Problems | Action 3 | Renewed body gasket, torqued bonnet bolts
Key Learning Points | Point 1 | Loose packing leaks hexane at the stem; over-tight packing makes the stem stick and the valve hunt.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Positioner Response & Loop
opl_no | OPL-LV-6701-04
opl_title | Positioner Response & Loop Check
sheet | 1 of 1
discipline | Instrument
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Improvement
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Thursday, 28 May 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-04 - Positioner_Response_Loop_Check.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains positioner response & loop check for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. Poor positioner tuning makes the level controller LIC-6701 hunt and the separator level cycle. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | De-energise and isolate the loop; place the function to bypass/inhibit under permit.
Safety Precautions | Precaution 2 | Inform the panel operator before working on any trip, valve or transmitter.
Safety Precautions | Precaution 3 | Take care with instrument air / hydraulic pressure when disconnecting tubing.
Safety Precautions | Precaution 4 | Verify intrinsic-safety / Ex integrity is restored before returning to service.
Safety Precautions | Precaution 5 | Wear correct PPE and follow ESD/override control procedures.
Tools & Materials | Tool 1 | HART communicator / positioner software (e.g. ValveLink)
Tools & Materials | Tool 2 | Loop calibrator & decade box / pressure source
Tools & Materials | Tool 3 | Digital multimeter and clamp meter
Tools & Materials | Tool 4 | Span/zero test gas or reference standards
Tools & Materials | Tool 5 | Torque screwdriver and small hand tools
Tools & Materials | Tool 6 | Certified test/inhibit permit
Procedure | Step 1 - Action | Step the LIC-6701 output and watch the valve response
Procedure | Step 1 - Check | Loop isolated / under permit
Procedure | Step 2 - Action | Check the ZSL/ZSH-6701 limit-switch feedback
Procedure | Step 2 - Check | Reference standard traceable
Procedure | Step 3 - Action | Tune the positioner gain for a stable, prompt travel
Procedure | Step 3 - Check | As-found & as-left recorded
Procedure | Step 4 - Action | Confirm there is no overshoot or stiction step
Procedure | Step 4 - Check | Trip / control action verified
Procedure | Step 5 - Action | Verify the valve seats fully at 4 mA (Class IV)
Procedure | Step 5 - Check | Return to service confirmed
Common Problems | Symptom 1 | LV-6701 not responding to LIC-6701, level control lost
Common Problems | Likely Cause 1 | Stem seized in PTFE packing (over-tightened + fines)
Common Problems | Action 1 | Freed stem, renewed packing, lubricated, re-stroked and calibrated
Common Problems | Symptom 2 | Positioner giving position error after drift
Common Problems | Likely Cause 2 | Positioner feedback out of calibration
Common Problems | Action 2 | Recalibrated DVC6200, updated firmware, verified travel
Common Problems | Symptom 3 | Hexane weeping at LV-6701 stem packing
Common Problems | Likely Cause 3 | PTFE V-ring packing worn
Common Problems | Action 3 | Renewed PTFE V-ring packing set, re-torqued gland
Key Learning Points | Point 1 | Poor positioner tuning makes the level controller LIC-6701 hunt and the separator level cycle.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Manual Bypass (HV-6701)
opl_no | OPL-LV-6701-05
opl_title | Manual Bypass (HV-6701) Operation
sheet | 1 of 1
discipline | Process / Operations
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Basic Knowledge
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Monday, 01 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-05 - Manual_Bypass_HV_6701_Operation.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains manual bypass (hv-6701) operation for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. The manual bypass lets operators keep the separator level safely while LV-6701 is isolated for maintenance. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | Obtain the correct operating permit and brief the shift team before the task.
Safety Precautions | Precaution 2 | Confirm hazardous fluids are isolated / inerted as required by procedure.
Safety Precautions | Precaution 3 | Beware of flammable, hot, or high-pressure fluids; wear the correct PPE.
Safety Precautions | Precaution 4 | Never defeat a safety interlock or trip without an authorised override permit.
Safety Precautions | Precaution 5 | Have emergency actions and communications ready before starting.
Tools & Materials | Tool 1 | Operating procedure & P&ID
Tools & Materials | Tool 2 | Radio / communication with panel
Tools & Materials | Tool 3 | Gas detector (O2 / LEL) as required
Tools & Materials | Tool 4 | Correct PPE for the fluid handled
Tools & Materials | Tool 5 | Sample containers & PPE for sampling
Tools & Materials | Tool 6 | Permit-to-work documentation
Procedure | Step 1 - Action | Notify the panel and take LIC-6701 to manual
Procedure | Step 1 - Check | Permit valid & briefed
Procedure | Step 2 - Action | Crack open the bypass HV-6701 slowly
Procedure | Step 2 - Check | Parameter within limit
Procedure | Step 3 - Action | Throttle HV-6701 to hold FA-6710 level using LT-6710
Procedure | Step 3 - Check | Interlock status confirmed
Procedure | Step 4 - Action | Isolate LV-6701 (close block valves) for the work
Procedure | Step 4 - Check | Change logged on DCS
Procedure | Step 5 - Action | Reverse the steps and re-establish auto control afterwards
Procedure | Step 5 - Check | Handover to next shift
Common Problems | Symptom 1 | LV-6701 isolation for planned maintenance
Common Problems | Likely Cause 1 | Planned - bypass used to hold level
Common Problems | Action 1 | Lined up HV-6701 manual bypass, isolated LV-6701 safely
Common Problems | Symptom 2 | LV-6701 not responding to LIC-6701, level control lost
Common Problems | Likely Cause 2 | Stem seized in PTFE packing (over-tightened + fines)
Common Problems | Action 2 | Freed stem, renewed packing, lubricated, re-stroked and calibrated
Common Problems | Symptom 3 | Manual handwheel jack on LV-6701 seized
Common Problems | Likely Cause 3 | Corrosion in handwheel thread
Common Problems | Action 3 | Overhauled handwheel assembly, greased thread
Key Learning Points | Point 1 | The manual bypass lets operators keep the separator level safely while LV-6701 is isolated for maintenance.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Fail-Closed & ESD Action
opl_no | OPL-LV-6701-06
opl_title | Fail-Closed & ESD Action Verification
sheet | 1 of 1
discipline | Instrument
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Basic Knowledge
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Friday, 05 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-06 - Fail_Closed_ESD_Action_Verification.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains fail-closed & esd action verification for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. On air failure or ESD (XV-6701), the valve must drive closed to prevent gas blow-by from the separator. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | De-energise and isolate the loop; place the function to bypass/inhibit under permit.
Safety Precautions | Precaution 2 | Inform the panel operator before working on any trip, valve or transmitter.
Safety Precautions | Precaution 3 | Take care with instrument air / hydraulic pressure when disconnecting tubing.
Safety Precautions | Precaution 4 | Verify intrinsic-safety / Ex integrity is restored before returning to service.
Safety Precautions | Precaution 5 | Wear correct PPE and follow ESD/override control procedures.
Tools & Materials | Tool 1 | HART communicator / positioner software (e.g. ValveLink)
Tools & Materials | Tool 2 | Loop calibrator & decade box / pressure source
Tools & Materials | Tool 3 | Digital multimeter and clamp meter
Tools & Materials | Tool 4 | Span/zero test gas or reference standards
Tools & Materials | Tool 5 | Torque screwdriver and small hand tools
Tools & Materials | Tool 6 | Certified test/inhibit permit
Procedure | Step 1 - Action | Trip the XV-6701 ESD solenoid during the test
Procedure | Step 1 - Check | Loop isolated / under permit
Procedure | Step 2 - Action | Confirm the actuator vents and the valve closes
Procedure | Step 2 - Check | Reference standard traceable
Procedure | Step 3 - Action | Time the full closure - it must be within 5 seconds
Procedure | Step 3 - Check | As-found & as-left recorded
Procedure | Step 4 - Action | Check the ZSL-6701 closed limit confirms on the DCS
Procedure | Step 4 - Check | Trip / control action verified
Procedure | Step 5 - Action | Reset the ESD and return the valve to auto
Procedure | Step 5 - Check | Return to service confirmed
Common Problems | Symptom 1 | LV-6701 not responding to LIC-6701, level control lost
Common Problems | Likely Cause 1 | Stem seized in PTFE packing (over-tightened + fines)
Common Problems | Action 1 | Freed stem, renewed packing, lubricated, re-stroked and calibrated
Common Problems | Symptom 2 | Positioner giving position error after drift
Common Problems | Likely Cause 2 | Positioner feedback out of calibration
Common Problems | Action 2 | Recalibrated DVC6200, updated firmware, verified travel
Common Problems | Symptom 3 | Hexane weeping at LV-6701 stem packing
Common Problems | Likely Cause 3 | PTFE V-ring packing worn
Common Problems | Action 3 | Renewed PTFE V-ring packing set, re-torqued gland
Key Learning Points | Point 1 | On air failure or ESD (XV-6701), the valve must drive closed to prevent gas blow-by from the separator.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.

## Actuator Diaphragm Inspection
opl_no | OPL-LV-6701-07
opl_title | Actuator Diaphragm Inspection (Fisher 667)
sheet | 1 of 1
discipline | Instrument
equipment_tag | LV-6701
equipment_name | SEPARATOR LEVEL CONTROL VALVE
area_unit | 6700 - LP SEPARATOR SYSTEM
related_interlock | SEQ-6701 (SIL 1)
pid_reference | TJC-LLD-PID-6701
classification | Improvement
aspect | P-Q-C-D-S-M-E
prepared_by | Panel Operator / Technician
reviewed_by | Vino Ardiansyah (EMP-1102)
approved_by | Zulkarnain Hasan (EMP-0901)
date_of_sharing | Tuesday, 09 June 2026
document_type | One Point Lesson (OPL)
source_file | OPL-LV-6701-07 - Actuator_Diaphragm_Inspection_Fisher_667.pdf
section | sub_field | value
Purpose / Objective | — | This One Point Lesson explains actuator diaphragm inspection (fisher 667) for LV-6701 (SEPARATOR LEVEL CONTROL VALVE) in the LP SEPARATOR SYSTEM. A ruptured actuator diaphragm causes loss of control and a continuous air leak; periodic inspection prevents surprise failures. The lesson gives operators and technicians the key knowledge and the correct step-by-step method so the task is done safely, correctly and consistently every time.
Safety Precautions | Precaution 1 | De-energise and isolate the loop; place the function to bypass/inhibit under permit.
Safety Precautions | Precaution 2 | Inform the panel operator before working on any trip, valve or transmitter.
Safety Precautions | Precaution 3 | Take care with instrument air / hydraulic pressure when disconnecting tubing.
Safety Precautions | Precaution 4 | Verify intrinsic-safety / Ex integrity is restored before returning to service.
Safety Precautions | Precaution 5 | Wear correct PPE and follow ESD/override control procedures.
Tools & Materials | Tool 1 | HART communicator / positioner software (e.g. ValveLink)
Tools & Materials | Tool 2 | Loop calibrator & decade box / pressure source
Tools & Materials | Tool 3 | Digital multimeter and clamp meter
Tools & Materials | Tool 4 | Span/zero test gas or reference standards
Tools & Materials | Tool 5 | Torque screwdriver and small hand tools
Tools & Materials | Tool 6 | Certified test/inhibit permit
Procedure | Step 1 - Action | Inspect the Fisher 667 diaphragm for cracks or perishing
Procedure | Step 1 - Check | Loop isolated / under permit
Procedure | Step 2 - Action | Check the bench set is 0.2-1.0 barg
Procedure | Step 2 - Check | Reference standard traceable
Procedure | Step 3 - Action | Replace the NBR/fabric diaphragm if hardened
Procedure | Step 3 - Check | As-found & as-left recorded
Procedure | Step 4 - Action | Re-stroke and recalibrate after any diaphragm work
Procedure | Step 4 - Check | Trip / control action verified
Procedure | Step 5 - Action | Confirm the spring range still gives full 38 mm travel
Procedure | Step 5 - Check | Return to service confirmed
Common Problems | Symptom 1 | LV-6701 not responding to LIC-6701, level control lost
Common Problems | Likely Cause 1 | Stem seized in PTFE packing (over-tightened + fines)
Common Problems | Action 1 | Freed stem, renewed packing, lubricated, re-stroked and calibrated
Common Problems | Symptom 2 | Positioner giving position error after drift
Common Problems | Likely Cause 2 | Positioner feedback out of calibration
Common Problems | Action 2 | Recalibrated DVC6200, updated firmware, verified travel
Common Problems | Symptom 3 | Hexane weeping at LV-6701 stem packing
Common Problems | Likely Cause 3 | PTFE V-ring packing worn
Common Problems | Action 3 | Renewed PTFE V-ring packing set, re-torqued gland
Key Learning Points | Point 1 | A ruptured actuator diaphragm causes loss of control and a continuous air leak; periodic inspection prevents surprise failures.
Key Learning Points | Point 2 | Respect the interlock SEQ-6701: e.g. LSHH-6710 trips at > 85 % - never defeat it without a permit.
Key Learning Points | Point 3 | Always cross-check the Datasheet limits and the P&ID TJC-LLD-PID-6701 before working on LV-6701.
Key Learning Points | Point 4 | Record the work in the equipment history so the Knowledge Hub stays the single source of truth.